## Master Sheet
Project | Suburb | Voltage at POC | Generation Technology | Generator Brand | Generator Model | Total Generation (kVA) | Transformer Size (kVA) | Protection and Control Systems | Secondary/Central Protection Relay (Yes/No) | Voltage Control and Reactive Power Capability | Export Control at PCC (Yes/No) | SLD of connection arrangment
1 | Clayton | HV | Synchronous - Gas | Caterpillar | 3516 | 12000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
2 | Springvale | HV | Synchronous - Gas | Caterpillar | 3516 | 4080 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
3 | Dandenong | HV | Synchronous - Gas | Leroy Somer | LSA 58 LBJ - GP | 6200 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
4 | Bangholme | HV | Synchronous - Gas | Deutz | TBG 620V16 | 11760 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
5 | Mount Eliza | LV | Synchronous - Diesel | Cummins | 715DQCC | 894 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
6 | Burwood East | LV | Synchronous - Diesel | Caterpillar | 3412 | 600 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
7 | Dandenong South | LV | Synchronous - Diesel | Cummins | C1100 D5 | 1100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
8 | Clayton | HV | Synchronous - Diesel | Caterpillar | C175-16 | 13000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
9 | Glen Waverley | LV | Induction - Hydro | TECO | Francis Hydro Turbine | 560 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
10 | Notting Hill | LV | Induction - Hydro | TECO | Francis Hydro Turbine | 450 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
11 | Rye | HV | Synchronous - Gas | Caterpillar | 3512 | 770 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
12 | Ashburton | LV | Synchronous - Gas | Schmitt Enertec | FMB-285-GSMK | 233 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
13 | Mount Waverley | LV | Microturbine | Capstone | C65 | 65 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
14 | Doncaster | LV | Synchronous - Gas | Guascor | SFGLD240 | 550 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
15 | Malvern | LV | Inverter - Solar | SMA | STP 15000TL STP 12000TL STP 10000TL | 37 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
16 | Noble Park | LV | DRUPS | MTU | 16V 4000 G63 | 6200 | 4000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
17 | Dandenong South | LV | Synchronous - Gas | GE Jenbacher | JMC 316 GS | 800 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
18 | Box Hill | LV | Inverter - Solar | SMA | STP15000TL | 75 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
19 | Caulfield | LV | Inverter - Solar | SMA | 6000A | 42 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
20 | Mount Martha | LV | Synchronous - Diesel | Mac Farlane | P1000P1/P1100E1 | 1100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
21 | Box Hill | HV | Synchronous - Gas | Caterpillar | G3516B | 1450 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
22 | Cheltenham | LV | Inverter - Solar | Canadian Solar | CS6P | 44 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
23 | Mulgrave | LV | Inverter - Solar | SMA | Triphase 15000TL | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
24 | Keysborough | LV | Inverter - Solar | Omnik | Omniksol-20k-TL | 99 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
25 | Dingley Village | LV | Inverter - Solar | Power One | PVI-10.0-OUTD Standard | 40 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
26 | Dandenong | LV | Inverter - Solar | PowerOne | PVI-10.0-OUTD-AU | 40 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
27 | Clayton | LV | Inverter - Microturbine | Capstone Microturbine | C200 C65 | 465 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
28 | Dandenong South | LV | Inverter - Solar | PowerOne | PVI-10.0-OUTD-AU | 40 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
29 | Dandenong South | LV | Inverter - Solar | ABB | PVS800-57-0100KW-A | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
30 | Box Hill | LV | Inverter - Microturbine | Capstone | C65-ICHP-DM | 130 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
31 | Frankston | LV | Inverter - Solar | SMA | STP15000TL | 135 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
32 | Malvern East | LV | Inverter - Solar | SMA | STP17000TL | 34 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
33 | Dandenong | LV | Inverter - Solar | PowerOne | PVI-10.0-OUTD-AU | 40 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
34 | Mitcham | LV | Inverter - Microturbine | Ensola | Turbec T100 | 200 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
35 | Dandenong | LV | Inverter - Solar | Diehl Ako | 22000TL 13000TL | 101 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
36 | Scoresby | LV | Inverter - Solar | SMA | STP 17000 | 34 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
37 | Hallam | LV | Inverter - Solar | PowerOne | PVI-12.5-TL-OUTD | 37.5 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
38 | Dandenong | LV | Inverter - Solar | PowerOne | PVI-10.0-OUTD-AU | 40 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
39 | Hawthorn | LV | Inverter - Solar | Delta Energy Systems | SOLIVIA 20TL1 | 60 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
40 | Dandenong South | LV | Inverter - Solar | PowerOne | PVI-12.5-TL-OUTD | 37.5 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
41 | Springvale | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 938.4 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
42 | Mitcham | LV | Inverter - Solar | PowerOne | PVI-12.5-TL-OUTD | 37.5 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
43 | Dandenong | LV | Inverter - Solar | SMA | STP10000TL | 40 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
44 | Carrum Downs | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD TRIO-20.0-TL-OUTD | 75.2 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
45 | Hallam | LV | Inverter - Solar | PowerOne | PVI-12.5-TL-OUTD | 75 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
46 | Dandenong | LV | Inverter - Solar | SMA | STP20000TLEE-10 | 40 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
47 | Dandenong South | LV | Inverter - Solar | Fronius | Agilo 100.0-3 | 300 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
48 | Doncaster | LV | Inverter - Microturbine | Turbec Spa | Turbec T100 | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
49 | Seaford | LV | Inverter - Solar | SMA | STP 15000TL STP 20000TL | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
50 | Springvale | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 248.4 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
51 | Dandenong | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD PVI-10.0-TL-OUTD | 92.8 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
52 | Springvale | LV | Inverter - Solar | Fronius | CL48.0 SYMO 20.0-3-M 1 x SYMO 10.0-3-M | 126 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
53 | Dandenong | LV | Inverter - Solar | SMA | STP 20000TL STP 10000TL | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
54 | Clayton | LV | Inverter - Solar | PowerOne | TRIO-20.0-TL-OUTD | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
55 | Edithvale | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD 1 x TRIO-20.0-TL-OUTD PVI-12.5-TL-OUTD | 72.6 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
56 | Hallam | LV | Inverter - Solar | ABB | PVI-10.0-TL-OUTD-AU PVI-12.5-TL-OUTD-AU | 65 | 300 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
57 | Nunawading | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD TRIO-20.0-TL-OUTD | 95.2 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
58 | Boneo | LV | Synchronous Generator | Caterpillar | Engine C32 Frame 1424 | 2250 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
59 | Moorooduc | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 82.8 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
60 | Glen Waverley | LV | Inverter - Solar | Enphase | M215-60-230-S22 | 50 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
61 | Dandenong | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 82.8 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
62 | Bon Beach | LV | Inverter - Solar | PowerOne | TRIO-20.0-TL-OUTD | 40 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
63 | Dandenong South | LV | Inverter - Solar | Fronius | CL36 | 36 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
64 | Donvale | LV | Inverter - Solar | PowerOne | TRIO-20.0-TL-OUTD PVI-6.0-TL-OUTD-AU PVI-8.0-TL-OUTD-AU PVI-10.0-TL-OUTD-AU PVI-12.5-TL-OUTD-AU | 56.5 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
65 | Cape Schanck | LV | Inverter - Solar | SMA APS | Tri-power 15000TL YC500 | 100 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
66 | Scoresby | LV | Inverter - Solar | SMA | 15000TL | 45 | 1500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
67 | Oakleigh | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 55.2 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
68 | Dandenong | LV | Inverter - Solar | SMA | STP20000TL | 40 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
69 | Mulgrave | LV | Inverter - Solar | Solar Max | SM15MT2 SM13MT2 | 56 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
70 | Mulgrave | LV | Inverter - Solar | Solar Max | SM15MT2 SM10MT2 | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
71 | Mulgrave | LV | Inverter - Solar | Solar Max | SM13MT2 SM10MT2 | 98 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
72 | Frankston | LV | Synchronous - Gas Asynchronous via Inverter - Gas Inverter - Gas Fuel Cell Asynchronous via Inverter - Gas | Stamford Yanmar Ceramic Fuel Cells Qnergy | UCI274H-311 CP4WE BlueGen 7.5kW | 136 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
73 | Safety Beach | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 182.8 | 100 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
74 | Springvale | LV | Inverter - Solar | SMA | 20000TL | 100 | 100 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
75 | Shoreham | LV | Inverter | PowerOne | TRIO-27.6-TL-OUTD TRIO-8.0-TL-OUTD | 63.2 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
76 | Caulfield South | LV | Synchronous - Gas | TEDOM | TS Micro T30 | 30 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
77 | Moorabbin | LV | Synchronous - Gas | Caterpillar | SR4 Frame 447 Arrangement 1938725 | 237 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
78 | Hallam | LV | Inverter - Solar | SMA | 15000TL | 45 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
79 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-320-GSMK | 260 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
80 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-500-GSMK | 400 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
81 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-430-GSMK | 350 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
82 | Dandenong South | LV | Inverter - Solar | Fronius | Agilo 100.0-3 | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
83 | Scoresby | LV | Inverter - Solar | SolarMax | SM15MT2 | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
84 | Braeside | LV | Inverter - Solar | SMA | STP20000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
85 | Wantirna South | LV | Inverter - Solar | SMA | STP15000TL 17000TL | 64 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
86 | Frankston | LV | Synchronous - Diesel | Caterpillar | 3512B 512DR7W Arrangement 252-3810 Frame 1447 | 3000 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
87 | Dandenong South | LV | Inverter - Solar | Fronius | Symo 15.0 3M Symo 10.0 3M | 75 | 100 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
88 | Dandenong | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD PVI-10.0-TL-OUTD | 92.8 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
89 | Nunawading | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD PVI-12.5-TL-OUTD | 92.7 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
90 | Seaford | LV | Inverter - Solar | Sun Grow Australia | SG10KTL | 40 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
91 | Braeside | LV | Inverter - Solar | SMA | STP15000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
92 | Templestowe | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 180 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
93 | Baxter | LV | Inverter - Solar | SMA | STP20000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
94 | Dandenong South | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 15.0-3-M | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
95 | Clayton | LV | Synchronous - Gas | TEDOM | TS Micro T30 | 30 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
96 | Somerville | LV | Inverter - Solar | ABB | PVI-12.5-TL-OUTD | 37.5 | 200 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
97 | Nunawading | LV | Inverter - Solar | SMA | STP25000TL | 50 | 2000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
98 | Templestowe | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD | 82.8 | 750 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
99 | Cheltenham | LV | Inverter - Solar | Zeversolar | Eversol TLC15k | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
100 | Box Hill | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
101 | Mount Waverley | LV | Induction - Hydro | WEG | 315L/J | 340 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
102 | Dandenong | LV | Induction - Hydro | Siemens | 1LA8353-4EB60-Z | 385 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
103 | Carrum Downs | LV | Inverter - Solar | Enphase | M215-60-230-S22 M250-60-230-S22 | 51 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
104 | Hallam | LV | Inverter - Solar | SMA | 17000TL | 51 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
105 | Mulgrave | LV | Inverter - Solar | SMA | 20000TL | 120 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
106 | Hallam | LV | Inverter - Solar | Fronius | Agilo 100.0-3 Outdoor | 100 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
107 | Malvern | LV | Inverter - Solar | SMA | STP25000TL-30 | 65 | 1000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
108 | Keysborough | LV | Inverter - Solar | SunGrow | SG30KTL SG20KTL | 50 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
109 | Moorabbin Airport | LV | Inverter - Solar | Solaredge | SE 17k | 99 | 1500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
110 | Caulfield | HV | Inverter - Solar | Enphase | M250 | 175 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
111 | St Kilda | LV | Inverter - Solar | Solaredge | SE 17k 16k | 170 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
112 | Dandenong South | LV | Inverter - Solar | Fronius | 20.0 3M 15.0 3M 8.2 3M | 255 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
113 | Hampton Park | LV | Inverter - Solar | Fronius | 20.0 3M 15.0 3M | 75 | 750 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
114 | Hampton Park | LV | Inverter - Solar | Fronius | Symo 20.0 3M | 60 | 1000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
115 | Dandenong | LV | Inverter - Solar | SMA | Tripower 25000TL | 75 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
116 | Dandenong South | LV | Inverter - Solar | SMA | Tripower 25000TL | 50 | 315 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
117 | Dandenong South | LV | Inverter - Solar | Zeversolar | 20000TL | 40 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
118 | Mentone | LV | Inverter - Solar | Zeversolar | Eversol TLC20k | 44 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
119 | Braeside | LV | Inverter - Solar | ABB | TRIO 27.6-OUTD | 52 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
120 | Clayton | HV | DRUPS | Pillar | Uniblock UBTD 2000 | 16000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
121 | Malvern | LV | Inverter - Solar | Schneider | Conext CL 25000E | 50 | 1500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
122 | Dandenong South | LV | Inverter - Solar | Fronius | 20.0 3M 17.0 3M | 68 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
123 | Dandenong | LV | Inverter - Solar | SMA | Tripower 25000TL | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
124 | Endeavour Hills | LV | Inverter - Solar | Fronius | Symo 17.5-3-M | 51 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
125 | Endeavour Hills | LV | Inverter - Solar | Fronius | Symo 17.5-3-M | 600 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
126 | Carrum Downs | LV | Inverter - Solar | SMA | STP2500TL | 50 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
127 | Seaford | LV | Inverter - Solar | SMA | Tripower | 96.5 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
128 | Mount Waverley | LV | Inverter - Solar | Solar Edge | SE16k-AUS | 72 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
129 | Braeside | LV | Inverter - Solar | Fronius | Symo 20.0.3 | 40 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
130 | Dingley Village | LV | Inverter - Solar | SMA | STP 25000TL | 100 | 1000 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
131 | Dandenong South | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 17.5-3-M | 62.92 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
132 | Baxter | LV | Inverter - Solar | SMA | STP20000TL-30 | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
133 | Keysborough | LV | Inverter - Solar | Fronius Power One | Symo 20.0-3-M Trio-27.6-OUTD | 87.6 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
134 | Springvale | LV | Inverter - Solar | Fronius | Symo 17.5-3-M | 35 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
135 | Carrum Downs | LV | Inverter - Solar | Goodwe | GW20K-DT | 40 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
136 | Dandenong South | LV | Inverter - Solar | Fronius | SYMO 17.5-3-M SYMO 15.0-3-M | 47.5 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
137 | Dandenong South | LV | Inverter - Solar | Enphase | M250-72-2LN-S2 | 99.98 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
138 | Braeside | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 80 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
139 | Dandenong South | HV | Inverter - Solar | SMA | STP60-10 | 900 | HV Customer | Type 2 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
140 | Mount Waverley | LV | Inverter - Solar | Fronius | Symo 17.5-3-M | 35 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
141 | Bangholme | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 40 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
142 | Ormond | LV | Inverter - Solar | Solis | 20K + 10K | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
143 | Clayton | LV | Inverter - Solar | Sungrow | SG20KLT | 100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
144 | Mount Waverley | HV | Inverter - Solar DRUPS | Fronius Piller | Symo 20.0-3-M UBR-625 | 645 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
145 | Glen Waverley | LV | Inverter - Solar | SMA | STP 20000 | 40 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
146 | Carrum Downs | LV | Inverter - Solar | One Solar | HS17000TL HS15000TL | 100 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
147 | Mulgrave | LV | Inverter - Solar | SMA | STP 25000 TL | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
148 | Seaford | LV | Inverter - Solar | Fronius | Symo 20 + 12.5 | 40 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
149 | Moorabbin | LV | Inverter - Solar | Fronius | Symo 20 + 12.5 | 32.5 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
150 | Keysborough | LV | Inverter - Solar | ABB | PVI-12.5-TL-OUTD | 100 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
151 | Baxter | LV | Inverter - Solar | SMA | TRIPOWER 20000TL | 40 | 100 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
152 | Braeside | LV | Inverter - Solar | Jiangsu Zeversolar SMA | Zeverlution Pro 33K STP20000 | 50 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
153 | Keysborough | LV | Inverter - Solar | Fronius | Agilo 100.0-3 Symo 20.0-3-M Symo 10.0-3-M | 150 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
154 | Carnegie | LV | Inverter - Solar | SMA | Sunny TRIPOWER 25000TL | 75 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
155 | Braeside | LV | Inverter - Solar | SMA | Sunny TRIPOWER 25000TL | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
156 | Dandenong | LV | Inverter - Solar | enPhase | M250 | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
157 | Dandenong South | LV | Inverter - Solar | Fronius | Eco 27.0-3-S Eco 15.0-3-M | 123 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
158 | Braeside | LV | Inverter - Solar | Fronius | Eco 25 | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
159 | Dandenong North | LV | Inverter - Solar | SMA | SUNNY TRIPOWER 20000TL | 40 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
160 | Scoresby | LV | Inverter - Solar | ABB | TRIO 27.6-OUTD TRIO 20.0-OUTD | 47.6 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
161 | Black Rock | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M | 45 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
162 | Clayton | LV | Inverter - Solar | Fronius | Symo-20.0-3-M Eco-25.0-3-S | 70 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
163 | Seaford | LV | Inverter - Solar | Fronius | Symo-20.0-3-M Eco-25.0-3-S | 70 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
164 | Dandenong | LV | Inverter - Solar | Fronius | Eco 27.0-3-S Symo 20.0-3-M Symo 10.0-3-M Eco 25.0-3-S | 82 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
165 | Dandenong South | LV | Inverter - Solar | FRONIUS | SYMO-20.0-3-M | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
166 | Caulfield South | LV | Inverter - Solar | Shanghai Surpass | SSE SPS 20KTL-B SSE SPS 30KTL-B | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
167 | Springvale | LV | Inverter - Solar | Fronius | Symo 10-3-M ECO 27.0-3-S | 91 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
168 | Dandenong South | LV | Inverter - Solar | ABB | TRIO 27.6-OUTD | 55.2 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
169 | Bangholme | LV | Inverter - Solar | Fronius | Eco 25.0-3-S | 100 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
170 | Glen Waverley | LV | Inverter - Solar | Fronius | Symo 10.0-3-M Eco 27.0-3-S | 91 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
171 | Cheltenham | LV | Inverter - Solar | Fronius | Symo 15.0.3-M Eco 27.0-3-S | 231 | 1000 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
172 | East Bentleigh | LV | Inverter - Solar | Shanghai Surpass | SSE SPS 25 KTL-B | 100 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
173 | Brighton East | LV | Inverter - Solar | Fronius | Eco 25.0-3-S | 100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
174 | Frankston | LV | Inverter - Solar | Fronius | Symo 17.5-3-M Eco 27.0-3-S | 99 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
175 | Doncaster | LV | Inverter - Solar | SMA | Sunny Tripower 25000TL SunnyBoy 1700TL SunnyBoy 1200TL | 81.3 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
176 | Moorabbin | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 39.5 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
177 | Dandenong South | LV | Microturbine | Capstone | C65 | 65 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
178 | Clayton | LV | Inverter - Solar | SMA | 20000TL-30 25000TL-30 | 95 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
179 | Braeside | LV | Inverter - Solar | SMA | SUNNY TRIPOWER 25000TL-30 | 50 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
180 | Scoresby | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 80 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
181 | Vermont | LV | Inverter - Solar | Fronius | Symo 10.0-3-M Eco 27.0-3-S | 91 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
182 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 99.98 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
183 | Doncaster | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
184 | Keysborough | LV | Inverter - Solar | SMA | STP 25000TL-30 | 50 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
185 | Moorabbin | LV | Inverter - Solar | SMA | STP 25000TL-30 | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
186 | Dandenong South | LV | Inverter - Solar | Fronius | Symo 8.2-3-M Eco 27.0-3-S | 197 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
187 | Mordialloc | LV | Inverter - Solar | Fronius | Symo 20 | 70 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
188 | Carrum Downs | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 40 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
189 | Vermont | LV | Inverter - Solar | ABB | Trio-27.6-TL-OUTD-400 Trio-20.0-TL-OUTD-400 | 99.84 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
190 | Moorabbin Airport | LV | Inverter - Solar | Fronius | Eco 25.0-3-S | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
191 | Hallam | LV | Inverter - Solar | Fronius | Eco 25.0-3-S | 150 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
192 | Keysborough | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-M | 47 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
193 | Keysborough | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-M | 47 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
194 | Springvale South | LV | Inverter - Solar | Fronius | Eco 25.0-3-S | 50 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
195 | Dandenong South | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD-400 TRIO-20.0-TL-OUTD-400 | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
196 | Mentone | LV | Inverter - Solar | SolarEdge | SE27.6K SE15K | 42.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
197 | Dandenong South | LV | Inverter - Solar | SMA | STP 25000TL | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
198 | Red Hill South | LV | Inverter - Solar | Solar Edge | SE27.6 | 55 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
199 | Somerville | LV | Inverter - Solar | Fronius | ECO 25 SYMO 20 | 100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
200 | Braeside | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD-400 | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
201 | Dandenong | LV | Synchronous - Diesel | Cummins | C825 D5 | 660 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
202 | Frankston | LV | Inverter - Solar | Fronius | Symo 20.0.3-M | 80 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
203 | Blackburn | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 17.5-3-M | 42.5 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
204 | Mulgrave | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 8.2-3-M | 35 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
205 | Mulgrave | LV | Inverter - Solar | Fronius | SYMO 20.0-3-S | 60 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
206 | Springvale | LV | Inverter - Solar | Enphase | S270 Microinverters | 42 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
207 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-M | 74 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
208 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 10.0-3-M | 118 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
209 | Moorabbin | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
210 | Bentleigh | LV | Inverter - Solar | Enphase | S270 Microinverters | 59 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
211 | Elsternwick | LV | Inverter - Solar | Fronius | Symo 20.0.3-M Symo 15.0.3-M Symo 10.0.3-M Symo 8.2.3-M | 93.2 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
212 | McKinnon | LV | Inverter - Solar | Enphase | S270 Microinverters | 60.48 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
213 | Ormond | LV | Inverter - Solar | Enphase | S270 Microinverters | 32.4 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
214 | Mornington | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50.4 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
215 | Dandenong | LV | Inverter - Solar | ABB | TRIO 27.6-TL-OUTD-S2X-400 | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
216 | Carrum Downs | LV | Inverter - Solar | SSE | SPS 30KTL SPS 20LTL-B | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
217 | Dandenong | LV | Inverter - Solar | Fronius | Eco 27.0-3-S | 54 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
218 | Sandringham | LV | Inverter - Solar | SMA | STP 25000TL STP 20000TL | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
219 | Beaumaris | LV | Inverter - Solar | SMA | STP 25000TL STP 20000TL | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
220 | Burwood | LV | Inverter - Solar | SolarEdge | SE27.6k | 55.2 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
221 | Heatherton | LV | Inverter - Solar | Enphase | S270 Microinverters | 38.07 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
222 | Hallam | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
223 | Braeside | LV | Inverter - Solar | GOODWE | GW20K-DT | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
224 | Dandenong South | LV | Inverter - Solar | SMA | Sunny Tripower 25000TL | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
225 | Vermont South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
226 | Keysborough | LV | Inverter - Solar | SolarEdge | SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
227 | Braeside | LV | Inverter - Solar | SolarEdge | SE27.6k SE15k | 97.8 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
228 | Brighton East | LV | Inverter - Solar | SMA | STP 25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
229 | Mordialloc | LV | Inverter - Solar | SolarEdge | SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
230 | Rowville | LV | Inverter - Solar | Fronius | Symo 20.0.3-M | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
231 | Dingley Village | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
232 | Braeside | LV | Inverter - Solar | Solis | Solis-30K | 180 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
233 | Bangholme | LV | Inverter - Solar | Fronius | Eco 27.0-3-S Symo 17.5-3-M Symo 5.0-3-M | 84 | 100 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
234 | Donvale | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 350 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
235 | Seaford | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 150 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
236 | Scoresby | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
237 | Somerville | LV | Inverter - Solar | Fronius | ECO 25.0-3-S Symo 15.0.3-M | 165 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
238 | Mordialloc | LV | Inverter - Solar | Fronius | Eco 25.0-3-S Eco 27.0-3-S | 52 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
239 | Nunawading | LV | Inverter - Solar | SMA | STP 20000TL-30 | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
240 | Seaford | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
241 | Dandenong | LV | Inverter - Solar | SMA | STP20000TL-30 STP25000TL-30 | 65 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
242 | Balnarring | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 75 | 100 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
243 | Clayton | LV | Inverter - Solar | SSE | SPS30KTL SPS25KTL-B | 195 | 200 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
244 | Carrum Downs | LV | Inverter - Solar | Goodwe | GW20K-DT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
245 | Scoresby | LV | Inverter - Solar | SolarEdge | SE27.6K | 138 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
246 | Scoresby | LV | Inverter - Solar | SolarEdge | SE27.6K | 165.6 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
247 | Scoresby | LV | Inverter - Solar | SolarEdge | SE27.6K | 138 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
248 | Braeside | LV | Inverter - Solar | SMA | STP25000TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
249 | Moorabbin | LV | Inverter - Solar | Fronius | Eco 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
250 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 57 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
251 | Rowville | LV | Inverter - Solar | Solar Edge | SE25k | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
252 | Heatherton | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
253 | Springvale | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 12.5-3-M | 87.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
254 | Cheltenham | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
255 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 17.5-3-M | 44.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
256 | Braeside | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 8.2-3-M | 89.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
257 | Doncaster | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S SYMO 20.0-3-M | 97 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
258 | Scoresby | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 10.0-3-M | 91 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
259 | Cheltenham | LV | Inverter - Solar | SMA | STP 25000TL-30 | 200 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
260 | Bentleigh | LV | Inverter - Solar | SMA | STP 20000TL-30 | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
261 | Hallam | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 40 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
262 | Flinders | LV | Inverter - Solar | Enphase Energy | S270-72-LN-2-AU | 64 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
263 | Carrum Downs | LV | Inverter - Solar | Fronius | Symo 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
264 | Carrum Downs | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD TRIO-20.0-TL-OUTD | 102.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
265 | Mordialloc | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
266 | Carrum Downs | LV | Inverter - Solar | ABB | TRIO-20.0-TL-OUTD | 60 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
267 | Lyndhurst | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 324 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
268 | Braeside | LV | Inverter - Solar | Solar Edge | SE25K | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
269 | Mentone | LV | Inverter - Solar | Zeversolar GoodWe | Eversol TLC20K GW25K-DT | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
270 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 8.2-3-M | 58.2 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
271 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 75 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
272 | Clayton South | LV | Inverter - Solar | SolarEdge | SE27.6K SE25k | 401 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
273 | Clayton South | HV | Inverter - Solar | SolarEdge | SE27.6K SE25K | 288 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
274 | Noble Park North | LV | Inverter - Solar | SolarEdge | SE27.6K | 193.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
275 | Dandenong | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 60 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
276 | Vermont | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
277 | Brighton | LV | Inverter - Solar | SolarEdge | SE27.6K SE25K SE17K | 94.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
278 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | SPS 30KTL SPS 20KTL-B | 90 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
279 | Carrum Downs | LV | Inverter - Solar | Huawei | SUN2000-33KTL | 240 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
280 | Noble Park North | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
281 | Moorabbin | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
282 | Scoresby | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3 M | 95 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
283 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M SYMO 12.5-3-M | 297.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
284 | Box Hill | LV | Inverter - Solar | Enphase | S230-60-LN-2-AU | 62.79 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
285 | Brighton | LV | Synchronous - Diesel | Cummins | C300 D5 | 300 | 300 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
286 | Hallam | LV | Inverter - Solar | SolarEdge | SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
287 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 162 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
288 | Mount Martha | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 17.5-3-S | 67.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
289 | Dandenong South | LV | Inverter - Solar | Jiangsu Goodwe Power | GW50K-MT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
290 | Dandenong | LV | Inverter - Solar | Fronius | SYMO 20.0 3-M | 80 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
291 | Dandenong | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
292 | Carrum Downs | LV | Inverter - Solar | Goodwe | GW20K-DT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
293 | Chelsea Heights | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
294 | Chelsea Heights | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
295 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 5.0-3-M | 86 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
296 | Moorooduc | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
297 | Clayton | LV | Inverter - Solar | Fronius | ECO 27.0-3-M SYMO 20.0-3-M | 47 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
298 | Dandenong South | LV | Inverter - Solar | Solis | Solis-30K Solis-15K | 214.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
299 | Dandenong South | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
300 | Keysborough | LV | Inverter - Solar | SMA | STP 25000TL-30 | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
301 | Braeside | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
302 | Pearcedale | LV | Inverter - Solar | Fronius | Fronius Eco 25.0-3-M Fronius Symo 20.0-3-M Fronius Eco 27.0-3-M Fronius Symo 17.5-3-M | 436.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
303 | Scoresby | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
304 | Braeside | LV | Inverter - Solar | Delta Electronics | RPI M30A | 300 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
305 | Noble Park | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
306 | Mornington | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
307 | Dandenong | LV | Inverter - Solar | SMA | STP 25000TL-30 | 50 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
308 | Dandenong South | LV | Inverter - Solar | ABB | TRIO 27.6-TL-OUTD | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
309 | Dandenong South | LV | Inverter - Solar | SMA | STP-50-40 | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
310 | Dandenong | LV | Inverter - Solar | SolarEdge | SE25K | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
311 | Rosebud | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
312 | Mornington | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
313 | Hastings | LV | Inverter - Solar | SolarEdge | SE27.6K SE15K | 42.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
314 | Hampton Park | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
315 | Moorabbin | LV | Inverter - Solar | ABB | TRIO-20.0-TL-OUTD | 60 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
316 | Malvern | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-M SYMO 17.5-3-M | 84.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
317 | Somers | LV | Inverter - Solar | ABB | TRIO-50.0-TL-OUTD | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
318 | Somers | LV | Inverter - Solar | ABB | TRIO-50.0-TL-OUTD | 200 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
319 | Clayton | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 15.0-3-M | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
320 | Dandenong | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
321 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 5.0-3-M | 86 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
322 | Braeside | LV | Inverter - Solar | SolarEdge | SE25K | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
323 | Heatherton | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
324 | Keysborough | LV | Inverter - Solar | Fronius | SYmo 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
325 | Heatherton | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
326 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 7.0 | 88 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
327 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25 Symo 20 | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
328 | Dandenong South | HV | Inverter - Solar | Huawei | SUN2000 33KTL | 1080 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
329 | Dandenong South | LV | Inverter - Solar | SMA | STP25000-TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
330 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 1030 | 1000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
331 | Dromana | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
332 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
333 | Rye | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
334 | Dromana | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
335 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
336 | Templestowe | LV | Inverter - Solar | Fronius | Symo 20.0-3-M Symo 15.0-3-M | 35 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
337 | Cheltenham | LV | Synchronous - Diesel | Cummins | C550D5 | 550 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
338 | Mulgrave | LV | Inverter - Solar | SMA | STP Tripower Core 1 STP 50-40 | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
339 | Cheltenham | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
340 | Keysborough | LV | Inverter - Solar | SMA | STP60000TL | 240 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
341 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | SPS30KTL SPS20KTL-B | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
342 | Blackburn | LV | Inverter - Solar | Solar Edge | SE17K | 34 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
343 | Skye | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 17.5-3-M | 92.5 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
344 | Doncaster East | LV | Inverter - Solar | SolarEdge | SE82.8K SE27.6K | 524.4 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
345 | Dandenong | LV | Inverter - Solar | SolarEdge | SE25K | 75 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
346 | Pearcedale | LV | Inverter - Solar | Fronius | ECO 27.0 Symo 7.0 | 88 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
347 | Carrum Downs | LV | Inverter - Solar | ABB | TRIO27.5 TL-OUTD | 95.2 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
348 | Glen Waverley | HV | Inverter - Solar | SMA | STP CORE1 50-40 | 250 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
349 | Mulgrave | LV | Inverter - Solar | Fronius | ECO27.0-3-S | 216 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
350 | Clayton | LV | Inverter - Solar | SMA | STP 25000TL-30 STP 20000TL-30 STP 10000TL-20 | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
351 | Mordialloc | LV | Inverter - Solar | Fronius | ECO25.0-3-S | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
352 | Hallam | LV | Inverter - Solar | ABB | TRIO-27.6-TL-OUTD TRIO-20.0-TL-OUTD | 95.2 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
353 | Box Hill | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
354 | Oakleigh South | LV | Inverter - Solar | Delta | M30A | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
355 | Ashwood | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 15.0-3-M | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
356 | Dandenong South | LV | Inverter - Solar | Fronius Diehl | ECO 25.0-3-S 22000 TL | 87.1 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
357 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | SPS30KTL SPS20KTL-B | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
358 | Dandenong South | LV | Inverter - Solar | ABB | TRIO-50.0-TL-OUTD | 300 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
359 | Braeside | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
360 | Red Hill | LV | Inverter - Solar | Fronius | Fronius ECO 27.0.3-S Fronius SYMO 15 | 96 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
361 | Dandenong South | LV | Inverter - Solar | Solar Edge | SE82.8k | 248.4 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
362 | Rosebud | LV | Inverter - Solar | SolarEdge | SE27.6k SE17k | 99.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
363 | Hastings | LV | Inverter - Solar | Fronius | ECO25.0-3-S | 75 | 50 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
364 | Dandenong | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
365 | Braeside | LV | Inverter - Solar | SMA | STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
366 | Dandenong | LV | Inverter - Solar | Fronius | Symo 20.0 3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
367 | Mulgrave | LV | Inverter - Solar | Fronius | Symo 20.0 3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
368 | Rosebud | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
369 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 12.5-3-M | 255.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
370 | Clayton South | LV | Inverter - Solar | Jiangsu GoodWe | GW50K-MT | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
371 | Keysborough | LV | Inverter - Solar | SolarEdge | SE82.8K | 331.2 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
372 | Cheltenham | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
373 | Mulgrave | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S | 79 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
374 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe Power | GW50K-MT | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
375 | Heatherton | LV | Inverter - Solar | SMA | STP25000-TL | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
376 | Clayton | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 17.5-3-M | 845 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
377 | Braeside | LV | Inverter - Solar | SMA | STP25000-TL | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
378 | Dandenong South | LV | Inverter - Solar | GoodWe | GW50K-MT | 100 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
379 | Dandenong South | LV | Inverter - Solar | SMA | STP25000TL-30 | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
380 | Nunawading | LV | Inverter - Solar | Fronius | ECO 27.0-3-5 SYMO 5.0-3-M | 86 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
381 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe | GW50K-MT | 100 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
382 | Dandenong South | LV | Inverter - Solar | Huawai | Sun2000 -33kTL | 120 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
383 | Braeside | LV | Inverter - Solar | Fronius | SYMO20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
384 | Frankston | LV | Inverter - Solar | Fronius | ECO 25.0-3-S ECO 27.0-3-S SYMO 20.0-3-M | 99 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
385 | Scoresby | LV | Inverter - Solar | Jiangsu GoodWe Power Supply | GW50K-MT | 100 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
386 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
387 | Noble Park | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 108 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
388 | Cheltenham | LV | Inverter - Solar | SMA | STP50-40TL | 100 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
389 | Cheltenham | LV | Inverter - Solar | SMA | STP25000-30TL | 100 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
390 | Chadstone | LV | Inverter - Solar | SMA | STP25000TL | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
391 | Mitcham | LV | Inverter - Solar | SMA | STP-50-40 | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
392 | Vermont | LV | Inverter - Solar | SMA | STP25000TL | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
393 | Dromana | LV | Inverter - Solar | Enphase | IQ 7 Microinverter | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
394 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 7.0-3-M | 88 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
395 | Box Hill North | LV | Inverter - Solar | Fronius | Fronius Eco 27kW Fronius Eco 15KW Fronius Eco 10KW | 79 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
396 | Oakleigh | LV | Inverter - Solar | Fronius | Symo 10kW Eco 25kW | 85 | 400 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
397 | Frankston South | LV | Inverter - Solar | Fronius | Symo 15.0-3-M | 60 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
398 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
399 | Moorabbin | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
400 | Cheltenham | LV | Inverter - Solar | SolarEdge | SE17.5K SE27.6K | 89.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
401 | Cheltenham | LV | Inverter - Solar | SolarEdge | SE17K SE27.6K | 99.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
402 | Clayton North | LV | Inverter - Solar | Fronius | ECO 27.0-3-S Symo 7.0-3-M | 169 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
403 | Clayton | LV | Inverter - Solar | Fronius | Eco 27.0-3-s | 81 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
404 | Braeside | LV | Inverter - Solar | GoodWe | GW50K-MT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
405 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
406 | Moorabbin | LV | Inverter | Fronius | ECO 25.0-3-S | 100 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
407 | Oakleigh | LV | Inverter - Solar | Solar Edge | SE82.8K | 165.6 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
408 | Oakleigh | LV | Inverter - Solar | Solar Edge | SE82.8K | 331.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
409 | Box Hill South | LV | Inverter - Solar | ABB | PVS-100-TL | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
410 | Dromana | LV | Inverter - Solar | ABB | PVS-100-TL | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
411 | Carrum | LV | Inverter - Solar | ABB | PVS-100-TL | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
412 | Wantirna South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S | 79 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
413 | Hastings | LV | Inverter - Solar | SMA | STP 25000TL-30 STP 15000TL-30 | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
414 | Fingal | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
415 | Rosebud | LV | Inverter - Solar | ABB | PVS-100-TL | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
416 | Dandenong South | LV | Inverter - Solar | ABB | PVS-100-TL | 1300 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
417 | Malvern | LV | Inverter - Solar | Fronius | Symo 20.0-3-M STP 10000TL-10 STP 12000TL-10 STP 15000TL-10 | 57 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
418 | Hallam | LV | Inverter - Solar | SolarEdge | SolarEdge SE25K | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
419 | Frankston | LV | Inverter - Solar | SMA | STP25000TL-30 STP20000TL-30 STP15000TL-30 | 170 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
420 | Frankston | LV | Inverter - Solar | SMA | STP20000TL-30 STP15000TL-30 STP25000TL-30 | 175 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
421 | Frankston | LV | Inverter - Solar | SMA | SMA STP25000TL-30 SMA STP20000TL-30 | 130 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
422 | Rosebud | LV | Inverter - Solar | SolarEdge | SE25K SE17K | 42 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
423 | Keysborough | LV | Inverter - Solar | SMA | STP20000TL | 40 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
424 | Keysborough | LV | Inverter - Solar | SMA | STP25000TL | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
425 | Braeside | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M ECO 27.0-3-M | 47 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
426 | Hastings | LV | Inverter - Solar | SolarEdge | SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
427 | Mulgrave | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
428 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 5.0-3-S | 86 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
429 | Malvern East | LV | Inverter - Solar | SolarEdge | SE25K | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
430 | Mount Waverley | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 162 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
431 | Hallam | LV | Inverter - Solar | SolarEdge | SE25K | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
432 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe Power | GW50K-MT | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
433 | Oakleigh | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 513 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
434 | Somerville | LV | Inverter - Solar | SolarEdge | SE25K | 115 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
435 | Dandenong South | LV | Inverter - Solar | Fronius Sungrow | ECO 27.0-3-S SYMO 8.2-3-M SG30KT2 | 92.2 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
436 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-S | 74 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
437 | Frankston | LV | Inverter - Solar | ABB | TRIO-20.0 TRIO 27.6 | 47.6 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
438 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S Symo 15.0-3-M | 99.82 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
439 | Dandenong South | LV | Inverter - Solar | GoodWe | GW50K-MT GW25K-DT | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
440 | Noble Park | LV | Inverter - Solar | SolarEdge | SE82.8K SE50K | 514 | 1750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
441 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3 | 189 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
442 | Sandringham | LV | Inverter - Solar | Fronius | 25-0-3-S ECO 20-0-3-S Symo | 95 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
443 | Dandenong | LV | Inverter - Solar | ABB | PVS-100-TL | 200 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
444 | Frankston | LV | Inverter - Solar | Solar Edge | SE82.8k SE27.6k | 193.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
445 | Scoresby | LV | Inverter - Solar | SolarEdge | SE 17K | 34 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
446 | Dandenong South | LV | Inverter - Solar | SMA | STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
447 | Caulfield | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 8.2-3-M | 83.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
448 | Clayton | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
449 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
450 | Hawthorn East | HV | Alternator - Diesel | Leroy & Somer | LSA 52.3 S7 – 4P | 3520 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
451 | Frankston | LV | Inverter - Solar | Solar Edge | SE82.8K SE27.6K | 358.8 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
452 | Bentleigh | LV | Inverter - Solar | Solar Edge | SE27.6 | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
453 | Frankston | LV | Inverter - Solar | Solar Edge | SE82.8K SE27.6K | 634.8 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
454 | Cheltenham | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
455 | Bentleigh East | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S SSE SPS 25 KTL-B | 206 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
456 | Wantirna South | LV | Inverter - Solar | Fronius Victron | SYMO 10.0-3-M SYMO 12.5-3-M SYMO 17.5-3-M SYMO 20.0-3-M Quattro 48/15000 | 180 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
457 | Keysborough | LV | Inverter - Solar | Jiangsu | GW50K-MT | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
458 | Mulgrave | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
459 | Kilda East | LV | Inverter - Solar | Fronius | ECO25 | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
460 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 20.0-3-M | 74 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
461 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO-27-0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
462 | Chelsea Heights | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
463 | Clayton | HV | Inverter - Solar | Solaredge | SE17K SE25K SE27.6K SE50K SE82.8K | 646.4 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
464 | Clayton | LV | Inverter - Solar | Solaredge | SE17K SE50K SE82.8K | 415.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
465 | Dandenong South | LV | Inverter - Solar | STP | 50-40, 15000TL | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
466 | Keysborough | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 8.2.0-3-M | 89.2 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
467 | Templestowe | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
468 | Cheltenham | LV | Inverter - Solar | SMA | TRIPOWER 25000LT | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
469 | Vermont | LV | Inverter - Solar | Fronius | ECO 27 | 54 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
470 | Merricks North | LV | Inverter - Solar | SolarEdge Fronius | SE50K SE25K SYMO 20.0-3-M | 195 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
471 | Tyabb | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
472 | Dandenong South | LV | Inverter - Solar | SMA | STP25000TL | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
473 | Bangholme | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO25.0-3-S | 79 | 100 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
474 | Scoresby | LV | Inverter - Solar | SolarEdge | SE82.8K SE50K SE27.6K | 436.4 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
475 | Braeside | HV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
476 | Rowville | LV | Inverter - Solar | SolarEdge | SE27.6K SE25K | 52.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
477 | Mount Eliza | LV | Inverter - Solar | SolarEdge | SE25K | 100 | 200 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
478 | Oakleigh | LV | Inverter - Solar | SMA | STP25000TL-30 CORE1 STP 50-40 | 75 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
479 | Dandenong | LV | Inverter - Solar | GoodWe | GW50K-MT | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
480 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
481 | Burwood East | LV | Inverter - Solar | SMA | STP60-10 | 840 | 3000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
482 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S | 52 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
483 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 15.0-3-M | 42 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
484 | Rosebud | LV | Inverter - Solar | SolarEdge | SE50K | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
485 | Dandenong South | LV | Inverter - Solar | Solis | SOLIS25K | 50 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
486 | Hastings | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
487 | Doncaster | LV | Inverter - Solar | Fronius | Symo 20.0-3-M Symo 15.0-3-M Symo 17.5-3-M | 70 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
488 | Burwood | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S SYMO 20.0-3-M SYMO 17.5-3-M SYMO 15.0-3-M SYMO 10.0-3-M | 432.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
489 | Braeside | LV | Inverter - Solar | Enphase | IQ7 Microinverter | 46 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
490 | Braeside | LV | Inverter - Solar | Fronius | SYMO 15.0-3-M ECO 27.0-3-S | 57 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
491 | Carrum Downs | LV | Inverter - Solar | Fronius | SYMO 27.0-3-S SYMO 12.5-3-S SYMO 15.0-3-S | 81.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
492 | Springvale | LV | Inverter - Solar | Fronius | SYMO 15.0-3-M SYMO 20.0-3-M SYMO 25.0-3-S SYMO 27.0-3-S | 214 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
493 | Scoresby | LV | Inverter - Regenerative | AVL | DynoForce ASM 4200/0.65-3 400 T | 928 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
494 | Brighton | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M | 45 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
495 | Dandenong | LV | Inverter - Solar | Fronius SMA | SYMO 20.0-3-M SYMO 10.0-3-M STP5000TL-20 | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
496 | Scoresby | LV | Inverter - Solar | Fronius | ECO 25.0-3-M SYMO 10.0-3-M | 60 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
497 | Moorabbin | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
498 | Hastings | LV | Inverter - Solar | Solar Edge | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
499 | Bangholme | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M | 95 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
500 | Hallam | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
501 | Dandenong South | LV | Inverter - Solar | Huawei | SUN2000-50KTL-M0 | 100 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
502 | Caulfield East | LV | Inverter - Solar | SMA | STP25000TL-30 STP15000TL-30 | 55 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
503 | Frankston | LV | Inverter - Solar | Fronius | Eco 27.0-3-S Symo 25.0-3-M | 538 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
504 | Dandenong South | HV | Inverter - Solar | Fronius | ECO 27.0-3-M ECO 25.0-3-S SYMO 15.0-3-M SYMO 10.0-3-M | 1065 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | HV Customer - Site Specific
505 | Keysborough | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
506 | Moorooduc | LV | Inverter - Solar | Solar Edge | SE50K | 50 | 50 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
507 | Burwood | LV | Inverter - Solar | zeversolar | Zeverlution Pro 30K | 60 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
508 | Nunawading | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
509 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
510 | Noble Park | LV | Inverter - Solar | Jiangsu GoodWe Power Supply | GW50K-MT | 100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
511 | Fingal | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 100 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
512 | Burwood | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
513 | Glen Waverley | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S | 79 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
514 | Dandenong South | LV | Inverter - Solar | ABB | ABB PVS-100 | 300 | 3000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
515 | Keysborough | LV | Inverter - Solar | Fronius | Fronius Symo 20.0-3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
516 | Moorabbin | LV | Inverter - Solar | Fronius | SYMO 15.0-3-M | 45 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
517 | Mornington | LV | Inverter - Solar | Fronius | FRONIUS SYMO 20.0-3-M FRONIUS SYMO 10.0-3-M | 75 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
518 | Mornington | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 10.0-3-M | 50 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
519 | Kooyong | LV | Inverter - Solar | SolarEdge | SE3000H SE6000H SE7300H SE8000H | 42.3 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
520 | Chelsea | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
521 | Mount Martha | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
522 | Bentleigh | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 17.5-3-M SYMO 15.0-3-M | 52.5 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
523 | Mornington | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
524 | Frankston | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 315 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
525 | Keysborough | LV | Inverter - Solar | Sungrow | SG 110CX | 110 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
526 | Mulgrave | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 3.0.3-M | 57 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
527 | Dandenong South | LV | Inverter - Solar | SolarEdge | SE27.6 | 82.8 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
528 | Burwood | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 17.5-3-M SYMO 15.0-3-M | 52.5 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
529 | Mentone | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 17.5-3-M | 92.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
530 | Cheltenham | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 54 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
531 | Box Hill | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 17.5.3-M | 79.5 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
532 | Rowville | HV | Inverter - Solar | Fronius | ECO27.0-3-S | 864 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | HV Customer - Site Specific
533 | Clayton | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 17.5-3-M | 67.5 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
534 | Lower Templestowe | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
535 | Clayton South | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
536 | Chelsea Heights | LV | Inverter - Solar | SMA | STP 50-40 | 50 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
537 | Dandenong South | LV | Inverter - Solar | Fronius | Fronius ECO 27.0-3-S Fronius SYMO 7.0-3-M | 61 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
538 | Carrum | LV | Inverter - Solar | Huawei Technologies | SUN2000-29.9KTL | 60 | 100 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
539 | Braeside | LV | Inverter - Solar | Solar Edge | SE82.8K | 82.8 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
540 | Dandenong South | LV | Inverter - Solar | GoodWe | GW50K-MT | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
541 | Glen Waverley | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M SYMO 12.5-3-M SYMO 10.0-3-M | 92.5 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
542 | Scoresby | LV | Inverter - Solar | SMA | STP 50-40 | 100 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
543 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
544 | Oakleigh South | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M SYMO 10.0-3-M | 70 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
545 | Mordialloc | LV | Inverter - Solar | SolarEdge | SE82.8K | 82.8 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
546 | Glen Waverley | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 40 | 300 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
547 | Dandenong South | LV | Inverter - Solar | Solar Edge | SE82.8K | 82.8 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
548 | Rosebud | LV | Inverter - Solar | Huawei | SUN2000-50KTL-M0 | 605 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
549 | Rosebud | LV | Inverter - Solar | Huawei | SUN2000-50KTL-M0 | 385 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
550 | Carrum Downs | LV | Inverter - Solar | Solar Edge | 82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
551 | Carrum Downs | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
552 | Carrum Downs | LV | Inverter - Solar | Fronius | SYMO 20.0-3-M | 80 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
553 | Mount Martha | LV | Synchronous - Biogas | 2G Caterpillar | 2G Agenitor 408 CT80 Caterpillar SR4B | 1100 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
554 | Ashburton | LV | Inverter - Solar | SMA | STP-2500TL-30 | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
555 | Dandenong South | LV | Inverter - Solar | Huawei | SUN2000-60KTL-M0 | 60 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
556 | Dandenong South | LV | Inverter - Solar | Goodwe | GW50K-WT | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
557 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 100 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
558 | Dingley Village | LV | Inverter - Solar | Enphase | IQ7+ | 99.66 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
559 | Breaside | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
560 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
561 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
562 | Hallam | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 10.0-3-M 1 x Symo 20.0-3-M | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
563 | Sommerville | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 84.9 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
564 | Keysborough | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
565 | Brighton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
566 | Mornington | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
567 | Nunawading | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 100 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
568 | Highett | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 47 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
569 | Nunawading | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
570 | Dromana | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 25 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
571 | Dandenong South | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 20.0-3-M | 90 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
572 | Brighton East | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 10.0-3-M 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 150 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
573 | Oakleigh | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 150 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
574 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 10.0-3-M 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 65 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
575 | Carrum Downs | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
576 | Carrum Downs | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 84.9 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
577 | Carrum Downs | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 47 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
578 | Mount Waverly | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
579 | Safety Beach | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M | 90 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
580 | Mulgrave | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
581 | Noble Park | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 200 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
582 | Moorabbin | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
583 | Sommerville | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 100 | 200 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
584 | Clayton | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP25000TL-30 | 125 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
585 | Cheltenham | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
586 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 1 x 25.0-3-S 1 x 27.0-3-S | 52 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
587 | Brighton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
588 | Hallam | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
589 | Frankston | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 100 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
590 | Heatherton | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
591 | Burwood | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x 27.0-3-S 1 x Symo 10.0-3-M 1 x Symo 15.0-3-M 1 x Symo 17.5-3-M 1 x Symo 20.0-3-M | 492.5 | 1500 | Type 3 | No | Must be within Distribution Code limits | Yes | Type 2
592 | Mt Waverley | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 10.0-3-M 1 x Symo 20.0-3-M | 50 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
593 | Hallam | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
594 | Box Hill | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 8.2-3-M | 89.2 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
595 | Braeside | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 50 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
596 | Caulfield North | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 12.5-3-M 1 x Symo 15.0-3-M 1 x Symo 17.5-3-M 1 x Symo 20.0-3-M | 90 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
597 | Keysborough | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP15000TL-30 1 x STP25000TL-30 | 90 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
598 | Doncaster East | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
599 | Carrum Downs | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
600 | Carrum Downs | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
601 | Dandenong | LV | Solar - Inverter | Fronius Fronius International GmbH | 1 x CL 36.0 1 x Symo 15.0-3-M | 51 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
602 | Braeside | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
603 | Bentleigh | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
604 | Mulgrave | LV | Solar - Inverter | SMA Australia Pty Ltd | STP20000TL-30 | 40 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
605 | Carrum Downs | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
606 | Glen Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 414 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
607 | Glen Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 331.2 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
608 | Notting Hill | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
609 | Tuerong | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 100 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
610 | Doncaster | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 47 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
611 | Dandenong South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | 1 x GW20K-DT 1 x GW60K-MT | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
612 | Hastings | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
613 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
614 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
615 | Somers | LV | Solar - Inverter | Enphase SMA Australia Pty Ltd | 1 x iQ7 1 x STP15000TL-30 | 45.5 | 200 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
616 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP20000TL-30 | 900 | HV Customer | Type 3 | No | Must be within Distribution Code limits | No | HV Customer - Site Specific
617 | Dandenong | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
618 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
619 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
620 | Dandenong | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP20000TL-30 1 x STP25000TL-30 | 235 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
621 | Braeside | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 10.0-3-M | 91 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
622 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
623 | Cape Schanck | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M | 140 | 2500 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
624 | Cape Schanck | LV | Solar - Inverter | Fronius Australia | 1 x 25.0-3-S 1 x 27.0-3-S | 79 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
625 | Cape Schanck | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 12.5-3-M 1 x Symo 20.0-3-M 1 x Symo 8.2-3-M | 80.7 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
626 | Doncaster East | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
627 | Blackburn | LV | Battery - Inverter Solar - Inverter | Huawei Technologies Co Ltd Sonnen GmbH | 1 x eco 8.2/12 1 x SUN2000-10kTL-M0 1 x SUN2000-50KTL-M0 | 73.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
628 | Somerville | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-20KTL 1 x SUN2000-29.9KTL 1 x SUN2000-33KTL | 84.9 | 100 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
629 | Dromana | LV | Solar - Inverter | Fronius Australia Samil Power | 1 x 27.0-3-S 1 x Solar Lake 15000TL 1 x Solar River 5200TL 1 x SR2K8TLA1 | 52.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
630 | Tyabb | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 89.7 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
631 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
632 | Braeside | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW30K-MT | 60 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
633 | Braeside | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW30K-MT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
634 | Brighton East | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
635 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
636 | Dandenong South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW29.9K-MT | 59.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
637 | Brighton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
638 | Mordialloc | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
639 | Notting Hill | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
640 | Braeside | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
641 | Braeside | LV | Solar - Inverter | Fronius International GmbH | 2 x Symo 20.0-3-M | 40 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
642 | Braeside | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 47 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
643 | Dandenong | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
644 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
645 | Nunawading | LV | Solar - Inverter | SMA SolarEdge Technologies Ltd | 1 x 6000A-1 1 x SE10K 1 x SE27.6K | 83.2 | 750 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
646 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
647 | Keysborough | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
648 | Frankston | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP15000TL-30 1 x STP25000TL-30 | 90 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
649 | Moorabbin | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 20.0-3-M | 45 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
650 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
651 | Dandenong | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
652 | Frankston | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
653 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
654 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
655 | Moorabbin Airport | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-20KTL | 44 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
656 | Red Hill | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x 27.0-3-S 1 x Symo 20.0-3-M | 99 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
657 | Moorabbin Airport | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
658 | Boneo | LV | Diesel - Synchronous Natural Gas - Synchronous | 2G Energy AG Caterpillar | 1 x Avus 500 plus BG 1 x C32 1100F | 1788 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
659 | Boneo | LV | Diesel - Synchronous Solar - Inverter | Caterpillar Fronius Australia | 1 x 27.0-3-S 1 x C32 1100F | 1127 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 5
660 | Dandenong South | HV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
661 | Clayton | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 20.0-3-M | 95 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
662 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
663 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 100 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
664 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
665 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP10000TL-20 1 x STP25000TL-30 | 235 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
666 | Noble Park North | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
667 | Boneo | LV | Natural Gas - Synchronous | 2G Energy AG | Avus 500 plus BG | 688 | 2000 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
668 | Nunawading | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
669 | Mulgrave | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 194.9 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
670 | Mulgrave | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 84.9 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
671 | Mulgrave | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 224.8 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
672 | Hastings | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
673 | Somerville | LV | Battery - Inverter Solar - Inverter | Fronius International GmbH Selectronic Australia | 1 x SPMC482-AU 1 x Symo 15.0-3-M | 52.5 | 25 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
674 | Glen Waverley | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
675 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
676 | Notting Hill | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
677 | Carrum Downs | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
678 | Blackburn | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 10.0-3-M 1 x Symo 20.0-3-M | 70 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
679 | Carrum Downs | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
680 | West Somerville | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP15000TL-30 1 x STP25000TL-30 | 90 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
681 | Brighton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
682 | Rowville | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE25K | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
683 | Oakleigh South | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-12KTL 1 x SUN2000-29.9KTL 1 x SUN2000-8KTL | 65.1 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
684 | Merricks | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
685 | Dandenong | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
686 | Springvale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
687 | Mornington | LV | Solar - Inverter | Enphase | IQ7A-72-M-INT | 47 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
688 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
689 | Dandenong South | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 220 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
690 | Clayton | HV | Diesel - Synchronous | Caterpillar | Cummins C2250D5 Caterpillar 1250F TRIO-27.6-TL-OUTD C1100D5 | 11682.8 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | Type 4
691 | Box Hill South | LV | Solar - Inverter | Fronius Australia Gsmart | 1 x 25.0-3-S 1 x GS500 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
692 | Mulgrave | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 100 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
693 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE27.6K | 82.8 | 4000 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
694 | Notting Hill | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
695 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
696 | Clayton | LV | Diesel - Synchronous | FG Wilson | 1 x P400E2 1 x P550E1 | 950 | 1000 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
697 | Huntingdale | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
698 | Clayton | HV | Diesel - Synchronous | Leroy Somer | LSA52.3 S6 | 4650 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | Type 4
699 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 63 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
700 | Mulgrave | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 425 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
701 | Frankston South | LV | Solar - Inverter | Fronius Australia Selectronic Australia | 1 x Primo 8.2-1 1 x SPMC482-AU | 47.1 | 63 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
702 | Tuerong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
703 | Tyabb | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
704 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
705 | BRAESIDE | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
706 | Mount Eliza | LV | Battery - Inverter Solar - Inverter | Fronius International GmbH Selectronic Australia | 1 x SPMC482-AU 1 x Symo 15.0-3-M | 52.5 | 315 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
707 | Springvale | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
708 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE33.3K | 66.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
709 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
710 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
711 | Keysborough | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 84.9 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
712 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd | SMA STP 10000TL (PV System) SMA STP 15000TL (PV System) SMA STP 20000TL (PV System) SMA STP 25000TL (PV System) SMA STP 50-40 (PV System) Enphase M250 (PV System) SMA STPS 60 (Battery Storage) Elpower Cleanisland 180 kVA (Battery Storage) MTU Gas Gen 1000kW | 3817.25 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | Type 5
713 | Springvale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
714 | Springvale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
715 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
716 | Doveton | LV | Solar - Inverter Solar and Battery - Inverter Wind - Microturbine | Britwind Fronius Australia Ningbo Deye Inverter Technology Co Ltd | 1 x 27.0-3-S 1 x R9000 1 x SUN-10K-SG04LP3-EU | 42 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
717 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 216 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
718 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
719 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
720 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
721 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
722 | Ashburton | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
723 | Scoresby | LV | Other Energy Source - Inverter Solar - Inverter | AVL SolarEdge Technologies Ltd | 1 x ASM 4200/0.65-3/400T 1 x SE82.8K | 1010.8 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
724 | Eumemmerring | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
725 | Carrum Downs | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
726 | Dandenong South | LV | Battery - Inverter Diesel - Synchronous Solar - Inverter | Shenzhen Sinexcel Electric Co Ltd SMA Solar Technology AG Staunch | 1 x DC13 072A 1 x PWG2-100K-EX 1 x STP 110-60 | 953 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
727 | Baxter | LV | Solar - Inverter | SMA Solar Technology | STP110-60 | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | Dandenong South | LV | Solar - Inverter | Fronius Australia | ECO 25.0-3-S | 75 | 500 | Type 4 | Yes | Must be within Distribution Code limits | No | Type 5
729 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
730 | Nunawading | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP25000TL-30 | 100 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
731 | Pearcedale | LV | Solar - Inverter | SYMO 20.0 | Fronius | 40 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
732 | Dandenong South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd SolarEdge | 1 x GW29.9K-MT 1 x SE30K | 59.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
733 | Scoresby | LV | Solar - Inverter | ABB Huawei Technologies Co Ltd | 1 x SUN2000-36KTL 1 x Trio20 1 x Trio27.6 | 87.6 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | Mulgrave | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 243 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
735 | Cheltenham | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-100KTL-M1 | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
736 | Blackburn | LV | Solar and Battery - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
737 | Dandenong South | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 10.0-3-M | 85 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
738 | Dandenong South | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 74 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
739 | Springvale South | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-100KTL-M1 | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
740 | Frankston | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 459 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
741 | Dandenong South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd Jiangsu Zeversolar New Energy Co Ltd | 1 x GW80K-MT 1 x TLC8000 | 88 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
742 | Moorabbin | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 496.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
743 | Mordialloc | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW25K-MT | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
744 | Blackburn North | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
745 | Carrum Downs | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 162 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
746 | Carrum Downs | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
747 | Bangholme | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 200 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
748 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
749 | Somerville | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 414 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
750 | Somerville | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE50K 1 x SE82.8K | 298.4 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
751 | Mornington | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
752 | Doncaster | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
753 | Bentleigh East | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
754 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
755 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 139.9 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
756 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 139.9 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
757 | Mulgrave | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
758 | Sandhurst | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
759 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
760 | Moorabbin Airport | LV | Solar - Inverter | SMA Australia Pty Ltd | STP110-60 | 550 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
761 | Chadstone | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE50K 1 x SE82.8K | 132.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
762 | Mornington | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
763 | Mckinnon | LV | Solar - Inverter | Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x Symo 8.2-3-M | 118.2 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
764 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
765 | Mount Eliza | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG10RT 1 x SG50CX | 60 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
766 | Mornington | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
767 | Brighton East | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
768 | Balnarring | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
769 | Keysborough | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 55 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
770 | Forest Hill | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
771 | Mt Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE33.3K | 33.3 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
772 | Noble Park North | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW50K-MT | 200 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
773 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP25000TL-30 | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
774 | Hallam | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
775 | Dandenong | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
776 | Keysborough | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 275 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
777 | Braeside | LV | Solar - Inverter | Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
778 | Chadstone | LV | Solar - Inverter Solar and Battery - Inverter | Fronius Australia Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX 1 x Symo 20.0-3-M 1 x Symo GEN24 10.0 Plus | 249.7 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
779 | Braeside | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
780 | Hallam | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE5000 1 x SE82.8K | 92.77 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
781 | Moorabbin | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
782 | Braeside | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP10.0-3AV-40 1 x STP25000TL-30 | 85 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
783 | Hallam | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
784 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP110-60 | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
785 | Braeside | LV | Solar - Inverter | Enphase Energy New Zealand Limited | IQ7A-72-2-US | 117.852 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
786 | Nunawading | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
787 | Wantirna South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GEP50-10 | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 3
788 | Moorabbin | LV | Solar - Inverter Solar and Battery - Inverter | Enphase Energy New Zealand Limited Fronius Australia Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x IQ7A-72-2-INT 1 x IQ7PLUS-72-E-INT 1 x SG50CX 1 x Symo 10.0-3-M 1 x Symo GEN24 10.0 Plus | 141.836 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
789 | Moorabbin | LV | Diesel - Synchronous Solar - Inverter | Caterpillar Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x 1938725 447 1 x SG110CX 1 x SG30CX 1 x Symo 5.0-3-M | 611.9 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 5
790 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
791 | Carrum Downs | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
792 | Seaford | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 89.7 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
793 | Noble Park | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
794 | Dromana | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | Solis-40K-5G | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
795 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
796 | Oakleigh South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP110-60 | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
797 | Donvale | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | 1 x SOLIS-30K-5G 1 x Solis-3P20K-4G | 52 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
798 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
799 | Oakleigh | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP25000TL-30 | 75 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
800 | Nunawading | LV | Solar and Battery - Inverter | Fronius Australia | 27.0-3-S | 81 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
801 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
802 | Patterson Lakes | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 60 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
803 | Springvale | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 10.0-3-M 1 x Symo 20.0-3-M | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
804 | Dandenong South | LV | Solar - Inverter | (ABB) Power-One Italy S.p.A | PVS-100-TL | 200 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
805 | Nunawading | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
806 | Chadstone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 320 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
807 | Chadstone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 129.9 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
808 | Chadstone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
809 | Chadstone | LV | Solar - Inverter | Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX 1 x Symo 10.0-3-M | 490 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
810 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
811 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
812 | Blackburn | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
813 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
814 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
815 | Dandenong | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
816 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
817 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
818 | Rosebud | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW29.9K-MT | 59.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
819 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
820 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
821 | Brighton East | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
822 | Keysborough | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
823 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 75 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
824 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 880 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
825 | Oakleigh South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
826 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 1 x 25.0-3-S 1 x Tauro 50-3-D | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
827 | Cheltenham | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 59.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
828 | Carnegie | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
829 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 880 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
830 | Brighton East | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
831 | Mornington | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
832 | Cheltenham | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
833 | Rosebud | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE100K 1 x SE82.8K | 182.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
834 | Doncaster | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
835 | Mulgrave | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG15RT 1 x SG50CX | 65 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
836 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
837 | Springvale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
838 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
839 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 440 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
840 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
841 | Dandenong South | LV | Solar - Inverter | Fronius Australia | Tauro Eco 100-3-D | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
842 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP25000TL-30 | 75 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
843 | Ashburton | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 110-60 1 x STP 50-40 | 160 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
844 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 139.9 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
845 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
846 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
847 | Burwood East | LV | Solar - Inverter | Fronius International GmbH | Symo 15.0-3-M | 45 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
848 | Mount Martha | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
849 | Oakleigh | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
850 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
851 | St Kilda | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd SMA Australia Pty Ltd | 1 x SMC6000TL 1 x SMC7000TL 1 x Solis-25K-5G-AU | 40.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
852 | Portsea | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
853 | Noble Park | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | Solis-50K | 55 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
854 | Crib Point | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 75 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
855 | Carrum Downs | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
856 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
857 | Portsea | LV | Solar - Inverter | (ABB) Power-One Italy S.p.A | PVS-100-TL | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
858 | Box Hill South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
859 | Box Hill | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M | 90 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
860 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
861 | Rowville | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
862 | Oakleigh South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
863 | Scoresby | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 440 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
864 | Mulgrave | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-100KTL-M1 | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
865 | Rowville | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
866 | Frankston South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE33.3K | 66.6 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
867 | Sandringham | LV | Solar - Inverter | Enphase Energy New Zealand Limited Fronius International GmbH | 1 x IQ7A-72-2-INT 1 x Symo 15.0-3-M | 44.274 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
868 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
869 | Highett | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
870 | Dromana | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
871 | Mont Albert | LV | Other Energy Source - Inverter Solar - Inverter Solar and Battery - Inverter | Fronius Australia Fronius International GmbH Selectronic Australia SMA Australia Pty Ltd | 1 x 25.0-3-S 1 x SB1100 1 x SPMC1201-6.0 1 x Symo 15.0-3-M | 97 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
872 | Nunawading | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
873 | Noble Park North | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 109.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
874 | Vermont | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE33.3K | 99.9 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
875 | Box Hill | LV | Solar - Inverter | Fronius International GmbH SMA Australia Pty Ltd | 1 x STP15000VA 1 x Symo 20.0-3-M | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
876 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 469.9 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
877 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
878 | Blackburn North | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
879 | Clayton South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
880 | Dandenong South | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | SOLS-30K | 90 | 50 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
881 | Dandenong South | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 110 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
882 | Clayton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
883 | Keysborough | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
884 | Dandenong South | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | Solis-30K | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
885 | Oakleigh South | LV | Solar - Inverter | SMA Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SB5000TL-20 1 x SG50CX | 55 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
886 | Bentleigh East | LV | Solar - Inverter | Fronius Australia Pty Ltd | TAURO 50-3-D | 200 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
887 | Bentleigh East | LV | Solar - Inverter | Fronius Australia Pty Ltd | TAURO 50-3-D | 100 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
888 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
889 | Rosebud | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
890 | St Kilda | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
891 | Blackburn | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 59.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
892 | Cheltenham | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 15.0-3-M | 57 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
893 | Hastings | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 89.7 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
894 | Bentleigh East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
895 | Dandenong South | LV | Battery - Inverter Solar - Inverter | Delta SolarEdge Technologies Ltd | 1 x PCS100HV 1 x SE82.8K | 2242 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
896 | Burwood | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 260 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
897 | Burwood | LV | Solar - Inverter | Greenstar Sungrow Power Supply Co Ltd | 1 x GS500A 1 x SG20RT 1 x SG50CX | 74 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
898 | Mordialloc | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
899 | Red Hill | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 10.0-3-M | 85 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
900 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
901 | Burwood | LV | Solar - Inverter | Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG20RT 1 x SG30CX 1 x Symo 10.0-3-M | 79.9 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
902 | Braeside | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
903 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
904 | Oakleigh South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
905 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
906 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
907 | Chelthenham | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 50-40 | 200 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
908 | Brighton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
909 | Frankston | LV | Solar - Inverter | Fronius Australia Pty Ltd | TAURO ECO 100-3-D | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
910 | Glen Iris | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
911 | Mordialloc | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
912 | Dandenong South | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | 1 x SOLIS-25KW-5G-AU 1 x SOLIS-40KW-5G-AU | 65 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
913 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG20RT | 40 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
914 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
915 | Keysborough | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 330 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
916 | Dandenong South | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
917 | Dandenong North | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 55 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
918 | Carrum Downs | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 54 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
919 | Dandenong South | HV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
920 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
921 | Bangholme | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 63 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
922 | Hampton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
923 | Donvale | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
924 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
925 | Glen Huntly | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
926 | Forest Hill | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
927 | Malvern | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
928 | Scoresby | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
929 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
930 | Dandenong | LV | Solar - Inverter | Fronius Australia | 25.0-3-S | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
931 | Mentone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
932 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
933 | Mordialloc | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
934 | Mordialloc | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 15.0-3-M | 84 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
935 | Noble Park | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 47 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
936 | Heatherton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
937 | Frankston | LV | Natural Gas - Microturbine Solar - Inverter | Capstone Sungrow Power Supply Co Ltd | 1 x C65 ICHP-DM 1 x SG110CX | 570 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
938 | Sandringham | LV | Solar - Inverter | Fronius International GmbH | Symo 15.0-3-M | 30 | 315 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
939 | Parkdale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
940 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
941 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
942 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE33.3K | 99.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
943 | Mitcham | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
944 | Pearcedale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
945 | Chelsea | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
946 | Keysborough | LV | Battery - Inverter Solar - Inverter | Sungrow Power Supply Co Ltd Tesla Motors Australia Pty Ltd | 1 x AC Powerwall 1 x SG110CX | 115 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
947 | Keysborough | LV | Battery - Inverter Solar - Inverter | Sungrow Power Supply Co Ltd Tesla Motors Australia Pty Ltd | 1 x AC Powerwall 1 x SG110CX | 115 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
948 | Dandenong South | LV | Solar - Inverter | Solis | Solis-30K-5G-AU | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
949 | Carnegie | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
950 | Clayton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
951 | Caulfield | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
952 | Mount Martha | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
953 | Moorabbin | LV | Solar - Inverter | Fronius Australia | 1 x 25.0-3-S 1 x 27.0-3-S | 208 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
954 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
955 | Seaford | LV | Solar - Inverter | (ABB) Power-One Italy S.p.A Fronius International GmbH | 1 x Symo 10.0-3-M 1 x Symo 20.0-3-M 1 x TRIO-27.6-TL-OUTD | 85.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
956 | Scoresby | LV | Solar - Inverter | Fronius International GmbH | Symo 15.0-3-M | 45 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
957 | Mulgrave | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
958 | Mulgrave | LV | Solar - Inverter | SMA Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX 1 x STP25000TL-30 | 295 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
959 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
960 | Dingley Village | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
961 | Mount Waverley | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 139.9 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
962 | Hallam | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
963 | Hallam | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
964 | Bentleigh East | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 20.0-3-M | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
965 | Seaford | LV | Solar - Inverter | Ginlong Technologies Co Ltd | S5-GC30K-AU | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
966 | Mount Waverley | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG30CX | 59.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
967 | Mulgrave | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW80K-MT | 160 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
968 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | TAURO 50-3-P | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
969 | Oakleigh South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
970 | Oakleigh South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
971 | Carrum Downs | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW50KN-MT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
972 | Frankston | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 165.6 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
973 | Dandening South | LV | Battery - Inverter Diesel - Synchronous Solar - Inverter | Staunch Sungrow Power Supply Co Ltd | 1 x SC50HV 1 x SG110CX 1 x STSG456 | 886 | 1500 | Type 3 | No | Must be within Distribution Code limits | Yes | Type 2
974 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
975 | Dromana | LV | Solar - Inverter | Ningbo Ginlong Technologies Co Ltd | 1 x S5-GC30K-AU 1 x S5-GC40K-AU | 70 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
976 | Noble Park | LV | Solar - Inverter | Enphase Energy New Zealand Limited | IQ7A-72-2-INT | 49.044 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
977 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
978 | Clayton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
979 | Mount Waverley | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 40 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
980 | Frankston | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 20.0-3-M | 70 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
981 | Brighton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG30CX | 59.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
982 | Moorabbin | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
983 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
984 | Dandenong North | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
985 | Brighton | LV | Solar - Inverter | Enphase Energy Australia Pty Ltd | IQ7A-72-2-INT | 35.868 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
986 | Mentone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
987 | Frankston | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
988 | Frankston | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
989 | Frankston | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
990 | Dandenong South | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 74 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
991 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
992 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
993 | Mount Waverley | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
994 | Clayton South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
995 | Frankston | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
996 | Springvale | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL-M3 | 59.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
997 | Malvern | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
998 | Carrum Downs | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
999 | Aspendale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG5.0RT 1 x SG50CX | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1000 | Box Hill South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1001 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd Sungrow Power Supply Co Ltd | 1 x SE5K 1 x SG110CX | 225 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1002 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Eco 25.0-3-S | 100 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1003 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1004 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1005 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1006 | Malvern East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1007 | Wantirna South | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-41 1 x STP-15000 TL–10 1 x STP-17000 TL–10 | 114 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1008 | Scoresby | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1009 | Rowville | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1010 | Clayton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1011 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1012 | Mount Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd SolarTec Sungrow Power Supply Co Ltd | 1 x SE5000 1 x SG110CX 1 x SG30CX 1 x SG50CX 1 x SolarTec5000 | 199.885 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1013 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1014 | Bentleigh | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1015 | Cheltenham | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
1016 | Clayton South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1017 | Doncaster East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1018 | Noble Park North | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
1019 | Mulgrave | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW80K-MT | 240 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1020 | Mount Waverley | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1021 | Scoresby | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1022 | Keysborough | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1023 | Keysborough | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1024 | Keysborough | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1025 | Elsternwick | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1026 | Mulgrave | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
1027 | Sorrento | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1028 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1029 | Glen Waverley | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1030 | Dingley Village | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 750 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
1031 | Mornington | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1032 | Langwarrin | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1033 | Nunawading | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 5
1034 | Malvern East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1035 | Clayton South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1036 | Nunawading | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1037 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1038 | Burwood East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1039 | Burwood East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1040 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 200 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1041 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro 50-3-D | 500 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1042 | Dandenong South | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-29.9KTL | 59.8 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1043 | Malvern East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 359.9 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1044 | Carrum Downs | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE30K | 300 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1045 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX | 79.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1046 | BRAESIDE | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1047 | SEAFORD | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG30CX | 59.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1048 | BRAESIDE | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE100K 1 x SE30K | 130 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1049 | Mentone | HV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG20RT | 240 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | Type 3
1050 | Burwood East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 270 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1051 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1052 | DANDENONG SOUTH | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro ECO 100-3-D | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1053 | KEYSBOROUGH | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1054 | NOTTING HILL | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1055 | NOBLE PARK NORTH | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1056 | Nunawading | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1057 | Glen Iris | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M | 89 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1058 | Rowville | LV | Solar - Inverter | Fronius Australia | Tauro Eco 100-3-D | 100 | 1000 | Type 3 | No | Must be within Distribution Code limits | No | Type 3
1059 | Dandenong South | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW100K-HT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1060 | DANDENONG SOUTH | LV | Solar - Inverter | Fronius | Tauro 100-3-D | 300 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1061 | Dandenong South | LV | Solar - Inverter | Aurora Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x PVI-10.0.-TL-OUTD 1 x Symo 6.0-3-M | 40 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1062 | Box Hill | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1063 | Mornington | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 80 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1064 | Caulfield South | LV | Battery - Inverter Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd Tesla Motors Australia Pty Ltd | 1 x AC Powerwall 1 x GW50KN-MT | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1065 | Oakleigh South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro 50-3-D | 100 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1066 | Dandenong South | LV | Solar - Inverter | Fronius International GmbH | Symo 20.0-3-M | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1067 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 550 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1068 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1069 | Scoresby | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1070 | Heatherton | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE100K | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1071 | Red Hill | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG20RT 1 x SG30CX | 49.9 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1072 | Carnegie | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1073 | Dandenong South | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1074 | Springvale | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1075 | Rosebud | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 139.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1076 | Templestowe Lower | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M 1 x Symo 8.2-3-M | 58.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
1077 | Blairgowrie | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG30CX | 59.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1078 | Braeside | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW60KN-MT | 60 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1079 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1080 | Hallam | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1081 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1082 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1083 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1084 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 270 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1085 | DROMANA | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE100K (AS4777-2 2020) | 200 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1086 | Mount Martha | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1087 | Keysborough | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1088 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1089 | Notting Hill | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 160 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1090 | Somerville | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D | 100 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1091 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1092 | DANDENONG SOUTH | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1093 | Mentone | LV | Solar - Inverter | Fronius Australia Pty Ltd Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M 1 x Tauro Eco 100-3-D | 350 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1094 | Mentone | LV | Solar - Inverter | Fronius Australia Fronius Australia Pty Ltd Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M 1 x Tauro 50-3-D 1 x Tauro Eco 100-3-D | 215 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1095 | MURRUMBEENA | LV | Battery - Inverter Solar - Inverter | SSE Tesla Motors Australia Pty Ltd | 1 x AC Powerwall 1 x SPS30KTL | 40 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1096 | Dandenong South | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE50K | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1097 | Clayton | LV | Solar - Inverter | Delta Electronics Inc Jiangsu GoodWe Power Supply Technology Co Ltd | 1 x GW60KN-MT 1 x RPI M20A | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1098 | Carrum Dow | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1099 | Mornington | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW60KN-MT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1100 | Mordialloc | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1101 | GLEN WAVERLEY | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG30CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 79.9 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1102 | Wheelers Hill | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE10000H 1 x SE10K | 60 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1103 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1104 | Mentone | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1105 | Box Hill South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 110 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1106 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1107 | Frankston | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1108 | DANDENONG SOUTH | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE100K (AS4777-2 2020) | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1109 | DANDENONG SOUTH | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 (AS4777-2 2020) | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1110 | NOBLE PARK NORTH | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG50CX (AS4777-2 2020) | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1111 | ROWVILLE | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 200 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1112 | ROWVILLE | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
1113 | WHEELERS HILL | LV | Solar - Inverter | Fimer SpA Sungrow Power Supply Co Ltd | 1 x PVS-20-TL-SX (AS4777-2 2020) 1 x SG110CX (AS4777-2 2020) 1 x SG30CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 380 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2

## Prot Types
Protection Type | Generator Protection Functions | Central/Secondary Prot Relay Functions | Comments
1 | Over Frequency | No Secondary Protection Relay | Applicable to inverter based installations with total capacity < 100kVA whose application was submitted prior to 1 May 2017
Under Frequency
Over Voltage
Under Voltage
2 | Over Frequency | Over Frequency | Applicable to inverter based installations with total capacity > 100kVA whose application was submitted prior to 1 May 2017
| Under Frequency | Under Frequency
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
ROCOF
Vector Shift
3 | Over Frequency | Over Frequency | Applicable to all negotiated inverter based installations whose application was submitted after or on 1 May 2017
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Sustained Over Voltage | Sustained Over Voltage
| Under Voltage | Under Voltage
| Soft Export Limit (where applicable) | ROCOF
Vector Shift
Reverse Power (where applicable)
4 | Over Frequency | Over Frequency | Applicable to all non-inverter based installations
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
| ROCOF | ROCOF
| Vector Shift | Vector Shift
| Reverse Power | Reverse Power (where applicable)
| Synch Check | Synch Check
Current based protection (O/C, E/F)
Negative Sequence Protection
Neutral Voltage Displacement (where possible) - e.g. HV customer not connected to a REFCL enabled feeder